## smartIAQ GridSet rev
Document #: |  | GPS-050-46-R26-SIAQSCHED
INTELLIGENT CLEAN AIR SYSTEMS
DEVICE SCHEDULE - smartIAQ GridSet SYSTEMS
TAG | LOCATION / AREA SERVED | MAX CFM | GPS MODEL NO. | QTY | COMPATIBLE POWER HUB | POWER HUB QTY | POWER HUB INLET / OUTLET VOLTAGE | FREQUENCY | POWER HUB MCA @ 120V* | MOCP | MAXIMUM NOISE CRITERION MAX | COMPLETEAQ FILTER SIZE | MIN ION OUTPUT (IONS/CC) | NOTES
|  | 150 | SIAQ2-DIST1S-DC-BK-48-NC |  | sIAQ-HB4 |  | 100 - 240VAC / 48 VDC | 60 Hertz | 2.5 A | 15 A | 25 | 20" x 20" x 2" | 160 Million | 1 to 13, 14, 15
|  | 150 | SIAQ2-DIST1S-DC-BK-48-BMS |  | sIAQ-HB4P-BN |  | 100 - 240VAC / 48 VDC | 60 Hertz | 2.5 A | 15 A | 25 | 20" x 20" x 2" | 160 Million | 1 to 13, 14, 15, 16
* Maximum MCA when (4) GridSet units connected to a single power hub
Notes Applicable to all units:
Select One: 1. Basis of Design: ASHRAE Standard 62.1 Indoor Air Quality Procedure utilizing smartIAQ GridSet; maximum area served per GridSet = 1500 sq ft
OR 1. Basis of Design: smartIAQ GridSet; maximum area served per GridSet = 1500 sq ft
2. Provide smartIAQ Hub-4 (or Hub-4 Pro) to power up to (4) GridSet units within 300' of smartIAQ Hub (120V-1-60 Input, 48 VDC output, 300W max load)
3. To power GridSet, connect each Gridset unit to a Power Hub via 48V CAT 5/5E cable with RJ45 connectors (also used for communication for Pro variants)
4. Complies with the current air cleaning design compound removal efficiencies as outlined in ASHRAE Standard 52.2 for particulate and ASHRAE 145.2, Laboratory Test Method for Assessing the Performance of Gas Phase Air Cleaning Systems
5. Complies with UL 2998, "Environmental Claim Validation Procedure for Zero Ozone Emissions from Air Cleaners". Must be CARB compliant for California applications.
6. Complies with ASHRAE Standard 241- 2023 Appendix A (3rd Party Safety Testing).
7. Variable speed Electronically Commutated Motor (ECM) is standard equipment.
8. Compatible with non-proprietary standard filters (IAQP application must use filters certified to ASHRAE 52.2 and 145.2 tesitng standards)
9. Coordinate mounting with ceiling construction type, ensuring compliance with local code for tie-offs or seismic restraint
10. Substitutions must be approved by the engineer
11. NPBI soft ionization technology is standard equipment
12. System shall be capable of actively tracking contaminant levels and operating fan speed to remediate and maximize filter life
13. Equipment shall be provided with a 3 year limited warranty, which may be extended to 5 years at time of purchase.
14. OPTIONAL NOTE TO ENGINEER: Equipment shall be provided with a minimum of (2) CompleteAQ filter sets by the manufacturer; initial filter set to be replaced at building commissioning
Notes to include for standard or base unit only (delete if not used)
15. Standard (base) system includes internal solid state sensor(s) to continuously monitor the following: Motion (Occupancy), Formaldehyde (HCHO), Temperature, Humidity.
Notes to include for Pro unit only (delete if not used)
15. Pro System includes internal solid state sensor(s) to continuously monitor the following: Motion (Occupancy), Formaldehyde (HCHO), Temperature, Humidity, Carbon Dioxide (CO2), TVOC, PM1.0, PM2.5, PM4.0, PM10.0.
16. Pro System shall provide BMS integration with BACnet MS/TP protocol via RS-485 connection to report air quality parameters and respond to speed commands, inhibit, or run.
NOTES TO DESIGNER COMPLETING THE TABLE:
Notes are set up in three sections to allow the designer to build the approriate table for drawings. Items 1 - 12 apply to all equipment in the table. Select the remianing notes based on application of the standard or base GridSet model or the Pro model.
For Note #1: should a project utilize air cleaning equipment for better indoor air, and not for the purpose of reducing the outside air, select the "Basis of Design: smartIAQ GridSet; maximum area served per GridSet = 1500 sq ft
- GPS GridSet model number SIAQ2-DIST1S-DC-BK-48-NC: standard (base) model, standalone operation; continuously monitors Motion (Occupancy), Formaldehyde (HCHO), Temperature, Humidity; cannot be configured to connect to building management system
Compatible Power Hub for standard (base) model = sIAQ-HB4
Capable of powering up to (4) GridSet units located within 300' of the Power Hub
- GPS GridSet model number SIAQ2-DIST1S-DC-BK-48-BMS: pro model, continuously monitors Motion (Occupancy), Formaldehyde (HCHO), Temperature, Humidity, Carbon Dioxide (CO2), TVOC, PM1.0, PM2.5, PM4.0, PM10.0; Bacnet enabled
Compatible Power Hub for Pro model options, select one:
- BACnet (MS/TP): sIAQ-HB4P-BN
© 2026 GPS Air
GPS Air is the owner of certain trademarks that appear in our materials. Please visit gpsair.com/trademarks for a list of our marks.

## smartIAQ
Document #: | GPS-050-46-R26-SIAQSCHED
INTELLIGENT CLEAN AIR SYSTEMS
DEVICE SCHEDULE - DISTRIBUTED smartIAQ® SYSTEMS | [11 empty] | GPS-FC48-AC | 200 Million | 10 | 1
AREA / TAG | NUMBER OF ZONES SERVED | MAX CFM | GPS MODEL | GPS QTY | VOLTAGE | MOUNTING LOCATION | MAX WATTS | MCA | OPERATING SOUND (NC) NOM / MAX | MIN ION OUTPUT (IONS/CC) | NOTES
- | 1 <= 1,000 sqft | 250 | SIAQ1-DIST1S-DC-BK-120 |  | 120-1-60 |  | 25 | 0.26 A | - / 26 | 160 Million | 1 to 12
- | 1 > 1,000 sqft | 500 | SIAQ1-DIST1L-DC-BK-120 |  | 120-1-60 |  | 100 | 1.05 A | 26 / 35 | 160 Million | 1 to 12
- | 2 | 250 | SIAQ1-DIST2-DC-BK-120 |  | 120-1-60 |  | 25 | 0.26 A | 26 / 35 | 160 Million | 1 to 12
- | 3 | 500 | SIAQ1-DIST3-DC-BK-120 |  | 120-1-60 |  | 100 | 1.05 A | 26 / 35 | 160 Million | 1 to 12
- | 4 | 500 | SIAQ1-DIST4-DC-BK-120 |  | 120-1-60 |  | 100 | 1.05 A | 26 / 35 | 160 Million | 1 to 12
Select One: 1. Basis of Design: ASHRAE Standard 62.1 Indoor Air Quality Procedure utilizing smartIAQ Distributed unit; maximum capacity per unit = 500 CFM | [11 empty] | CV
OR 1. Basis of Design: smartIAQ Distributed unit; maximum capacity per unit = 500 CFM
2. Substitutions must be approved by the engineer
3. Complies with the current air cleaning design compound removal efficiencies as outlined in ASHRAE Standard 52.2 for particulate and ASHRAE 145.2, Laboratory Test Method for Assessing the Performance of Gas Phase Air Cleaning Systems
4. Complies with UL 2998, "Environmental Claim Validation Procedure for Zero Ozone Emissions from Air Cleaners". Must be CARB compliant for California applications. | [11 empty] | VAV
5. Complies with ASHRAE Standard 241- 2023 Appendix A (3rd Party Safety Testing).
6. System should employ internal solid state sensor(s) to continuously monitor the following: Carbon Dioxide (CO2), Formaldehyde (HCHO), TVOC, PM1.0, PM2.5, PM4.0, PM10.0, Temperature, Humidity.
7. System shall be capable of actively tracking contaminant levels and operating fan speed to remediate and maximize filter life
8. [As required] Serial BacNet interface to report air quality parameters and respond to speed commands, inhibit, or run. | [11 empty] | GPS-FC48-AC | 4800 | 1 to 8
9. Variable speed Electronically Commutated Motor (ECM) is standard equipment. | [13 empty] | 1 to 6
10. Compatible with non-proprietary standard filters (IAQP application must use filters certified to ASHRAE 52.2 and 145.2 tesitng standards) | [11 empty] | GPS-FC24-AC | 2400 | 1 to 8
11. Equipment shall be provided with a 3 year limited warranty, which may be extended to 5 years at time of purchase.
12. Optional Power Supply for 203/230/277/347-1-60: (SIAQ1-UNVX).
[12 empty] | GPS-FC48-AC | 200 Million | 10 | 1
DEVICE SCHEDULE - CENTRALIZED smartIAQ SYSTEMS
AREA / TAG | NUMBER OF ZONES SERVED | MAX CFM | GPS MODEL | GPS QTY | VOLTAGE | MOUNTING LOCATION | MAX WATTS | MCA | NOMINAL OPERATING SOUND (NC) | MIN ION OUTPUT (IONS/CC) | NOTES
- | see note 3 | 700 | SIAQ1-CENT-DC-BK-UNV |  | 120/203/230/347-1-60 |  | 200 | 2.08 A | 26 / 35 | 160 Million | 1 to 13
CV
Select One: 1. Basis of Design: ASHRAE Standard 62.1 Indoor Air Quality Procedure utilizing smartIAQ Centralized unit; maximum capacity per unit = 700 CFM
OR 1. Basis of Design: smartIAQ Centralized unit; maximum capacity per unit = 700 CFM
2. Substitutions must be approved by the engineer
3. Intelligent Clean Air System integrates into central HVAC system in a sidestream configuration.
4. Multiple units can be installed in parallel to each other for higher capacity systems.
5. Complies with the current air cleaning design compound removal efficiencies as outlined in ASHRAE Standard 52.2 for particulate and ASHRAE 145.2, Laboratory Test Method for Assessing the Performance of Gas Phase Air Cleaning Systems
6. Complies with UL 2998, "Environmental Claim Validation Procedure for Zero Ozone Emissions from Air Cleaners". Must be CARB compliant for California applications.
7. Proof of compliance to ASHRAE 241- 2023 Appendix A (3rd Party Safety Testing).
8. System should employ internal solid state sensor(s) to continuously monitor the following: Carbon Dioxide (CO2), Formaldehyde (HCHO), TVOC, PM1.0, PM2.5, PM4.0, PM10.0, Temperature, Humidity. | [11 empty] | GPS-FC48-AC | 4800 | 1 to 8
9. System shall be capable of actively tracking contaminant levels and operating fan speed to remediate and maximize filter life | [13 empty] | 1 to 6
10. [As required] Serial BacNet interface to report air quality parameters and respond to speed commands, inhibit, or run. | [11 empty] | GPS-FC24-AC | 2400 | 1 to 8
11. Variable speed Electronically Commutated Motor (ECM) is standard equipment.
12. Compatible with non-proprietary standard filters (IAQP application must use filters certified to ASHRAE 52.2 and 145.2 tesitng standards)
13. Equipment shall be provided with a 3 year limited warranty, which may be extended to 5 years at time of purchase.
1
DEVICE SCHEDULE - PERFORMANCE smartIAQ SYSTEMS
AREA / TAG | NUMBER OF ZONES SERVED | MAX CFM | GPS MODEL | GPS QTY | VOLTAGE | MOUNTING LOCATION | MAX WATTS | MCA | NOMINAL OPERATING SOUND (NC) | MIN ION OUTPUT (IONS/CC) | NOTES
- | 1 | 500 | SIAQ1-PERF-CC-BK-120 |  | 120/1/60 |  | 100 | 1.05 A | 26 / 35 | 160 Million | 1 to 11
CV
Select One: 1. :Basis of Design: smartIAQ Performance unit; minimum capacity per unit = 250 CFM, maximum capacity per unit = 500 CFM
OR 1. Basis of Design: ASHRAE Standard 62.1 Indoor Air Quality Procedure utilizing smartIAQ Performance unit; minimum capacity per unit = 250 CFM, maximum capacity per unit = 500 CFM
2. Substitutions must be approved by the engineer | [11 empty] | VAV
3. Complies with the current air cleaning design compound removal efficiencies as outlined in ASHRAE Standard 52.2 for particulate and ASHRAE 145.2, Laboratory Test Method for Assessing the Performance of Gas Phase Air Cleaning Systems
4. Complies with UL 2998, "Environmental Claim Validation Procedure for Zero Ozone Emissions from Air Cleaners". Must be CARB compliant for California applications.
5. Complies with ASHRAE Standard 241- 2023 Appendix A (3rd Party Safety Testing).
6. System should employ internal solid state sensor(s) to continuously monitor the following: Carbon Dioxide (CO2), Formaldehyde (HCHO), TVOC, PM1.0, PM2.5, PM4.0, PM10.0, Temperature, Humidity.
7. System shall be capable of actively tracking contaminant levels and operating fan speed to remediate and maximize filter life | [11 empty] | GPS-FC48-AC | 4800 | 1 to 8
8. [As required] Serial BacNet interface to report air quality parameters and respond to speed commands, inhibit, or run. | [13 empty] | 1 to 6
9. Variable speed Electronically Commutated Motor (ECM) is standard equipment. | [11 empty] | GPS-FC24-AC | 2400 | 1 to 8
10. Compatible with non-proprietary standard filters (IAQP application must use filters certified to ASHRAE 52.2 and 145.2 tesitng standards)
11. Equipment shall be provided with a 3 year limited warranty, which may be extended to 5 years at time of purchase.
12. Optional Power Supply for 203/230/277/347-1-60: (SIAQ1-UNVX).
© 2026 GPS Air
GPS Air is the owner of certain trademarks that appear in our materials. Please visit gpsair.com/trademarks for a list of our marks.

## Validation (hidden)
DM Model Dropdown | Voltages Dropdown | Self Cleaning Model Pulldown | FC Model Dropdown (Line 43) | FC Model Dropdown (Line 44) | Voltages Dropdown
|  |  | GPS-FC-24-AC |  | 24-240
GPS-DM-48-AC | 24 | GPS-FC-48-AC | GPS-FC-3-BAS | GPS-FC-24-AC | 120-240
GPS-DM-2-AC | 120 | GPS-FC-24-AC |  | GPS-FC-3T-BAS
| 208 | GPS-CI-2-AC
240
277